Main Power A309
UPS (460 kW for ID)
non-redundant
LEE_A0393
400 V ~115 kW
22 x PDU 400V ~ av. 5.2 kW
LEE_A0394
400 V ~115 kW
22 x PDU 400V ~ av. 5.2 kW
LEE_A0395
400 V ~115 kW
22 x PDU 400V ~ av. 5.2 kW
LEE_A0396
400 V ~115 kW
22 x PDU 400V ~ av. 5.2 kW

---
PDU connection
PDU 400 V ~
av. 5.2 kW
L1A 230 V ~ 16 A
L1B 230 V ~ 16 A
L2A 230 V ~ 16 A
L2B 230 V ~ 16 A
L3A 230 V ~16 A
L3B 230 V ~ 16 A

---
PDU – a star connection
PDU 400 V ~
av. 5.2 kW
L1A 230 V ~ 16 A
L1B 230 V ~ 16 A
L2A 230 V ~ 16 A
L2B 230 V ~ 16 A
L3A 230 V ~16 A
L3B 230 V ~ 16 A

---
Calculating the maximum current on the CBs
As show, the UPS delivers a maximum of 115 kW per switchboard cabinet.
Before this threshold is reached a warning will be issued.
Based on this the maximum current can be computed, as shown on the next slides.
This can be done either by using the inner voltage (UY , 230 V 1ph AC) or the outer voltage (U, 400 V 3ph AC).
The outer voltage is the geometrical sum of the inner voltage, therefore

---
Power calculus for one switchboard cabinet
Simplifications
  - Think of computers as resistive loads
  - Avoiding complex power
  - Observed power factors
Effective Power
  - =>
  - For and
Conclusion: Even with a rather bad power factor of 0.9 it is not possible to release a 200 A CB in the cabinet.

---
Power calculus for one cabinet outer voltage
Simplifications
  - Think of computers as resistive loads
  - Avoiding complex power
Effective Power
  - =>
  - For and
  - (rounding difference to previous slide)

---
Conclusion
The limiting factor on the electrical power is the power delivered by the UPSs which is at maximum 115 kW per cabinet (460 kW total).
With the available power it is not possible to release the cabinet’s 200 A CB by overload. The CBs are designed to protect the wires not to limit the available power (germ. “Leitungsschutzschalter”)
It is not possible to release the 32 A CBs in the cabinets by overload unless there is a malfunction of the 16 A CBs in the PDU.
Bottom line: LEE A309 is electrically well engineered – no availability issues reaching the limits of the UPSs possible.

---
Measures
Ensure that the UPS alerting is working and that we get a warning when 80% of the power budget is being consumed (not necessarily automated).
Get a regular energy consumption bill by FM (quarterly or monthly).
Check the Riedo power concentrator output monthly to avoid unbalanced installations.
Decide if an additional UPS is needed to uphold a n+1 redundancy.
Decide on further development on LEE A on ITS GL level.

---
One PDU outer power
Maximum effective power on a single PDU with a power factor of 0.98
Outer power 400 V, CBs adding up to 32 A per phase.

---
One PDU inner power
Maximum effective power on a phase of a PDU with a power factor of 0.98
For the whole PDU the effective power adds up arithmetically
It is unlikely that all CBs are fully exhausted. An average factor of maximum 0.75 can be assumed: