## Slide 1: Advanced DAQ and Quench Detection using FPGA based UQDS systems
Jens Steckert, Reiner Denz, Tomasz Podzorny, Jelena Spasic David Bailey, Daniel Blasco Serrano, Magnus Christensen, Adam Hollos, Josef Kopal, Surbhi Mundra, Guzman Martin, Andrzej Skoczen, Dragos Gabriel Vancea, Vito Vizziello & MPE-EP Colleagues
Thanks to SM18 & Test bench crews for their support !

## Slide 2: Introduction
Motivation
HiLumi comprises of many different new and complex magnets:  Big variety but small numbers per item (compared to LHC)
MQXFA
MCBXFA
MQSXF
MCBXFB
MCBRDHA
MBRD
SC Link
MQXFB
MBXF
MCBRDVA
Basic concept
Design one generic system with enough resources to perform quench detection and monitoring of all HiLumi circuit elements
Base new design on programmable Logic (FPGA) in combination with a number of galvanically isolated front-end channels
Design is a quench detection AND measurement system
TE-MPE-EP designed, built and operates the LHC quench detection system comprising 13000 interlocking quench detectors and a total of 20k active circuit boards located all over LHC’s 27km tunnel

## Slide 3: System overview (UQDSv2)
Insulated font-end channel
Insulated font-end channel
Insulated font-end channel
.
.
.
Processing Element
(FPGA)
Interlocks &
Active
triggers
Up to 16 channels galvanic insulation
Digital platform
Communication interface
Power Supply (monitored) 230V AC
Power Supply (monitored) 230V AC
Passive mid-plane
Voltage taps

## Slide 4: Measurement channel
Galvanically isolated measurement channel ~2.5kV/1h, 5kV/1s
Fully differential architecture with very good common mode rejection
High performance 20-bit, 1Msps ADC
Robust input protection (1kV/1s differential)
Excellent signal quality
Parameter | Value
Resolution (20-bit ADC) | 105 nV/LSB .. 48 uV/LSB
ADC speed | Up to 909 kS/s
Analogue bandwidth | 120 kHz @ G=1 (customizable)
Active input voltage range | +/-50 mV (G=450) .. +/-22.5 V (G=1) (1.2kV with divider)
Max differential input voltage | 1 kV/10 s
Galvanic insulation | 2.5 kV/1h, 5kV/1s

## Slide 5: Analog channel measurements
Total Harmonic Distortion (THD)
Noise
Common mode rejection ratio (CMRR)
Bandwidth
Linearity
Total Harmonic distortion
<-110dBfs @ 1kHz
Noise: 2.3 .. 2.6 ppm standard deviation
Common mode rejection vs frequency
> 100dB
Linearity (calibrated): < 5ppm
(uncalibrated ~0.1%)

## Slide 6: System Properties
Excellent analogue performance both in AC and DC measurements
Real time digital signal processing on FPGA (filters, gain/offset correction)
Quench detection algorithms or other user code in FPGA
Various hard interlock options and standards (modular design)
Post-Mortem event recording with large buffers
Absolute time synchronization on microsecond level using Ethernet PTP
Fast logging up to 10kHz via EDAQ (Currently R&D to increase to 100..200kHz)

## Slide 7: Gateware structure – Multi-platform Multi-purpose
Hardware abstraction Layer Hardware specific interfaces Static for each hardware
Interfaces to payload code “config block”
Superconducting Link protection
Inner triplet protection
Swiss Knife
Common UQDS services (interfaces, communication & control)
Payload code
“config block”

## Slide 8: Multi-purpose Gateware on multiple Hardware
HAL
Hardware abstraction Layer
Hardware abstraction Layer
Common Logic & communication interface
Config blocks
Hardware abstraction Layer
Gateware compiled from common code base
Common Repository
Application specific parts defined in HDL and Spreadsheet
Automatic VHDL code generation for register map and interfaces
Toolchain heavily scripted (Python & tcl)
Hardware-in-the loop verification techniques
Common Codebase
Spreadsheet (config block specific)
Configuration files & HAL
Toolchain
 Toolchain allows selection of target hardware and config block

## Slide 9: Gateware structure – “config block” examples
Swiss Knife
Q3 protection
IT corrector Prot.

## Slide 10: UQDS – more than the “blue boxes”
It’s a hardware and Gateware framework providing building blocks for:
  Programmable logic & Flexible Gateware framework
  High performance isolated analogue input channels
  Interlocks & digital I/O
  Communication solution with us precision (with EDAQ)
Allows for rapid development of new electronics due to existing “Lego bricks”
UQDSv3 channel (adapted)
UQDSv3 channel (adapted)
UQDS FPGA
Block
Example:
DQQDL_004 for LHC main dipoles < 2 Months to prototype
FPGA
Gateware
ADC channels
Power supplies
Interlocks
Testing framework
Standard API
Fast Logging
And more

## Slide 11
UQDS ecosystem
UQDSv2 16 isolated channels
33 configurations … and counting
~120 systems produced and in use (usage: see next slides)
3 config blocks planned
60 boards produced production of 630 boards pending
Versatile quench detector board for
LHC CONS
Bus-bar and current lead monitor DQQBSv2
2 config blocks
122 installed in LHC Production of 500 more started
Image Description Configuration Status
1
Protection Devices Supervision Unit for HiLumi
10 systems produced for IT STRING
3 configurations planned
100 analog channels

## Slide 12: UQDS ecosystem
UQDSv3 Up to 32 isolated channels,
Faster acquisition speed
Optimized mechanics
34 pieces installed in LHC around experiments
DQQDL_004 Upgrade of LHC dipole quench detectors
 Evolutionary upgrades and extensions of the ecosystem
Large production of 2600 pieces Variable threshold & radiation tolerant Prototypes in testing
Image Description Configuration Status
At least 7 for LHC HiLumi
Rad tol upgrade for QDS crate controller for ion run. FPGA with UQDS firmware, rapid development thanks to ready building blocks
1 test ,1 production
Evolutionary upgrade of UQDSv2 Baseline for the HiLumi First prototype in testing Production of pre-series started

## Slide 13: EDAQ – timing and communication for UQDS
Ethernet based solution with ~ 1000x the throughput compared to field bus used in LHC (~10Mbit per client)
Timing precision > 1000x better than previous solution using ethernet precision timing protocol  absolute precision better than 1 us
Connects to services such as logging and post mortem
R&D for high bandwidth communication using gigabit ethernet started !
Q2 quench in cluster F1

## Slide 14: EDAQ & UQDS combined
PDPAC card is implementing core UQDS and EDAQ functionality on one PCB
Polyvalent use case, same hardware used for:
  UQDSv3 controller: General UQDS firmware and EDAQ for communication
  PDSU controller: Special firmware for protection devices supervision, trigger matrix/controller EDAQ com.
  CLIQ controller: Crate controller & EDAQ for communication
PDPACv2 adds faster uC to FPGA link and gigabit ethernet capable microcontroller
UQDS
EDAQ

## Slide 15: Applications at CERN
FAIR magnet test stand in B180
18 x UQDSv2
FRESCA facility B163
8 x UQDSv2
C3
C7
C20
SM18 cluster F1 & F2 (HiLumi Q2 & SC Link testing)
30 x UQDSv2
SM18 HiLumi STRING
35 x UQDSv2
LHC tunnel
C22
C23
C19
C3
C24
122 x DQQBSv2 around IPs
40 x DQAMGS babysitter
SM18 clusters A, B, C, D, G
10 x UQDSv2
C6
 Full exploitation of flexible Gateware to follow the rich test program in SM18
C28
C24
C30
C33
…

## Slide 16: Applications outside CERN
FREIA test facility Uppsala Sweden
2x UQDSv2
For test of HiLumi magnets
IFJ PAN Krakow Poland
2 x UQDSv2
C3
PSI Villingen Switzerland
2x UQDSv2 for SC Magnet Lab
7x UQDSv2 quench detection of SLS2.0 2x super bend magnet
C8
C16
300 uV
50Hz moving average filter
Data: M. Duda PSI
INFN LASA (Milano)
Collaboration agreement in preparation for 2x UQDS & Training

## Slide 17: Outlook
Software support other than the rigid CERN controls stack is could be improved
Work has started on a Python based library for communication and configuration
  Handles communication protocol via: UART, SPI, I2C or EDAQ
  Abstracts settings and allows user friendly configuration of the system (no register settings in hex anymore)
Plans for a more user-friendly GUI (based on the library)
Currently R&D for much faster communication speeds which would allow continuous logging with 100..200kHz via Ethernet
R&D for novel QD methods: DAC channel to inject signals into magnet
Next big challenge after STRING will be HiLumi with about 175 UQDS3 systems

## Slide 18: Summary
Established platform with full system integration in CERN controls services
Inhouse solution with full control about all elements  We can cope with obsolescence etc…
Quite unique feature set
  High performance measurement channels with galvanic insulation of ~5kV peak
  FPGA for real time processing of data & hardware interlocks
  Radiation tolerant versions available
Flexible adaptable design which can serve many purposes !
Focus now on completion of units for IT STRING
UQDS3 development ongoing