## Slide 1: Thermal-Hydraulic cryogenic studies : CS margin exploration WPMAG Final meeting 15/01/2026 François Bonne

## Slide 2: Thermal-Hydraulic cryogenic studies
Case studied : how to increase the margin (or reduce the superconducting amount) of the a CS at reasonable cryogenic cost?
Lower the inlet temperature
Lower the Inlet Temperature when needed
Depressurize the loop
We will take advantage of the CS margin being low for a very short amount of time

## Slide 3: SHe helium loop
Pipe | Section | Diameter (mm) | Length (m)
Upstream and downstream the conductor | Close to the bath | 125 | 33.5
 | Middle | 100 | 35.2
 | Close to the conductor | 50 | 1.6
Upstream and downstream the circulator |  | 125 | 2.0
Pipe length and diameter (inspired by WPDES)
Simcryogenics to model the CS with a Supercritical helium loop  Relevant behavior of a CICC including its cooling process circuit

## Slide 4: Current scenario and AC losses
(time not linear)
The same current scenario is applied since 2022 to help with comparisons. The CS design has not changed for the same reason

## Slide 5: Context : Margin loss
Return pipes
Supply pipes
HXPS1 to circulator pipes
Circulator to HXPS2 pipes
HXPS1
HXPS2
Bath 1 : 4,4K
Magnet
LP
HP
Cold compressor
Joule Thomson valve
HP1
Load valve
Unload valve
LP1
Magnet
6 bars
4,5 K
5 bars
4,6K
Initially, the model used pressure boundaries to compute margin.
Then, implementation of SHe cryogenic loop and thermal buffering in the model has been done. Each ones contributing of a more relevant behavior of the system but causing margin loss.
Pressure boundaries
SHe cryogenic loop
With thermal buffer : +0,4K allowed inside the bath
0,75 K lost due to implementation of cryogenic loop and around 50 mK lost due to thermal buffering (0,4K maximal temperature increase allowed inside the bath).

## Slide 6: How to regain margin using different configurations ?
Lower the inlet temperature
Lower the Inlet Temperature when needed
Depressurize the loop

## Slide 7: How to regain margin ? Single bath configuration thermally bufferized
Return pipes
Supply pipes
HXPS1 to circulator pipes
Circulator to HXPS2 pipes
HXPS1
HXPS2
Bath 1 : 4,4K
Magnet
LP
HP
Cold compressor
Joule Thomson valve
HP1
Load valve
Unload valve
LP1
Decrease bath temperature until the magnet reaches suitable temperature margin
Bath 1 : T < 4,4K
Easiest way to regain margin
High « cryogenic » cost as cooler SHe during all the cycle
1 bath configuration with a nominal CICC pressure of 6 bars

## Slide 8: How to regain margin ? : Single bath configuration, thermal buffer impact on margin
Bath temperature set to 3,43 K to obtain 1,5 K margin
 | Minimal margin (K)
With thermal buffering | 1,5046
Without thermal buffering | 1,5379
33 mK margin lost due to thermal buffering

## Slide 9: How to regain margin ? : Single bath configuration thermally bufferized
0,5 K increase
Bath temperature set to 3,43K to obtain 1,5 K margin
Return pipes
Supply pipes
HXPS1 to circulator pipes
Circulator to HXPS2 pipes
HXPS1
HXPS2
Magnet
LP
HP
Cold compressor
Joule Thomson valve
HP1
Load valve
Unload valve
LP1
Bath 1 : 3,43K
Volume = 50,4 m3

## Slide 10
How to regain margin : 2 baths configurations
Return pipes
Supply pipes
HXPS1 to circulator pipes
Circulator to HXPS2 pipes
HXPS1
HXPS2
Bath 1 : 4,4K
Magnet
LP
HP
Cold compressor
Joule Thomson valve
HP1
LP1
Bath 2 : T° < T° Bath 1
2 baths configuration with a nominal CICC pressure of 6 bars
Cryogenic cost more optimized. Second bath used only preventively to cool down SHe before breakdown

## Slide 11
Return pipes
Supply pipes
HXPS1 to circulator pipes
Circulator to HXPS2 pipes
HXPS1
HXPS2
Magnet
LP
HP
Cold compressor
Joule Thomson valve
HP1
LP1
Bath 2 : 3,02 K
Volume = 37,6 m3
How to regain margin : 2 baths configurations
Bath 1 : 4,4K
Volume = 50,4 m3
0,25 to 0,4 K increase
0,5 K increase

## Slide 12: How to regain margin ? : 2 bath configuration, thermal buffer impact on margin
 | Minimal margin (K)
With thermal buffering | 1,498
Without thermal buffering | 1,626
128 mK margin lost due to thermal buffering

## Slide 13: Simcryogenics : 10 bars ramp discharge at a nominal CICC pressure of 14 bars
Return pipes
Supply pipes
HXPS1 to circulator pipes
Circulator to HXPS2 pipes
HXPS1
HXPS2
Bath 1 : 4,4K
Magnet
LP
Cold compressor
HP1
Unload valve
Load valve
HP
10 bars ramp discharge with a nominal CICC pressure of 14 bars
Optimal cryogenic cost as SHe is cooled down only the necessary time (about a dozen of seconds instead of hundreds)
New concept

## Slide 14: Simcryogenics : 14 bars ramp discharge
0,35 to 0,4 K increase
Bath 1 : 4,4K
Volume = 50,4 m3
Storage bath : 4,4 K
Volume = 12 m3
Return pipes
Supply pipes
HXPS1 to circulator pipes
Circulator to HXPS2 pipes
HXPS1
HXPS2
Magnet
LP
Cold compressor
HP1
Unload valve
Load valve
HP
Gaz outlet
Liq outlet

## Slide 15: How to regain margin ? :, thermal buffer impact on margin
 | Minimal margin (K)
With thermal buffering | 1,5075
Without thermal buffering | 1,52
12,9 mK margin lost due to thermal buffering

## Slide 16: Comparison of thermally bufferized configurations : Margin
10 bars pre cooling by ramping the discharge produce less total exergy compared to others configurations.
More particularly : 28,2 % less than single bath configuration and 9,1 % less than 2 baths configurations
 | Total exergy (GJ)
Single bath | 5,18
2 baths | 4,1
10 bars ramp discharge | 3,72

## Slide 17: Conclusion
Magin lost using a realistic cryogenic configuration can be retreive using different cryogenic schemes
Among the presented configuration, the 10 bars ramp discharge with a nominal CICC pressure of 14 bars shows the best results in terms of energy consumtion production (28% and 9,1 % less than single bath and 2 bath configurations respectively)
The lost margin has been recovered and it could be 1,5 K again using this solution

## Slide 18: Bonus : Combination of 2 cryogenic processes : 2 baths and 10 bars ramp discharge

## Slide 19
Return pipes
Supply pipes
HXPS1 to circulator pipes
HXPS1
HXPS2
LP
HP
Cold compressor
Joule Thomson valve
HP1
LP1
Bath 2 : 3,02 K
Volume = 37,6 m3
Magnet
Nominal pressure = 14 bars
Bath 1 : 4,4 K
Volume = 50,4 m3
HXPS3
Storage bath : 4,4 K
Volume = 12 m3
Unload valve
Liq outlet
Gas outlet
HP2
Load valve
Combination of 2 cryogenic processes : 2 baths and 10 bars ramp discharge with a nominal CICC pressure of 14 bars
1,5 K threshold
2,09 K
The combination of the 2 cryogenic processes allows to gain 590 mK of margin

## Slide 20: Preliminary Costs exploration : Reduction of the CS superconducting amont (simply proportionally, needs to be refine)

## Slide 21: Cryogenic costs and supraconductor cost (M€)
Calculation has been performed with the same current scenario, with a 1,5 K margin

## Slide 22: Total cost (M€) : Cryogenic cost + Supraconductor cost
Points which cryogenic cost starts increse to be higher than supraconductor costs diminution.
10 bars ramp discharge configuration allows to save more than 120 M€ by reducing size of the supraconductor.
Calculation has been performed with the same current scenario, with a 1,5 K margin

## Slide 23: Conclusion
The cryogenic process can have a large impact on the CS operation and specifically its margin
Using appropriate process can lead to
an increased margin
and / or
a CS superconducting amount reduction
And needs to be investigate more into details